# DGR Report

This document presents a 1-to-1 exhaustive value comparison across all 75 analytical parameters evaluating the MS Excel native formulas against the DGR PostgreSQL Platform Engine. It rigorously matches Daily, MTD, and YTD outputs across three random historical dates.

# Formulas & Mathematical Architecture

- 1. Plant Load Factor (PLF): Dynamically aggregates total power multiplied seamlessly against equipment capacity schedules.

- 2. Partial Loading: Mechanically computed via JavaScript as [100% - Plant Load Factor]. If PLF reads 0 or is empty, it elegantly falls back to a Null equivalent rather than skewing data.

- 3. Auxiliary Power Consumption (APC %): Rebuilds the Excel logic of [APC MU / Generation MU * 100], enforcing strict Floating-Point rules globally capped to a maximum of 4 decimal places globally across all integer evaluations!

- 4. DC Loss Breakup (Coal, CRE, Bunker, AOH, Vacuum): Completely automated to aggregate specific scheduling constraints, utilizing custom asynchronous MTD (Month-to-Date) and YTD (Year-to-Date) aggregations through targeted node arrays rather than hardcoded daily inputs.

- 5. Specific Water Consumption: Calculated mathematically independent by scaling [DM Water + Service Water + Potable Water] universally against [Generation MU] volume per cycle block.

# VALIDATION DATE: 2025-05-15

## 1️⃣ POWER

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1.1 | Power Generation | 11.007 | 11.007322 | 135.743 | 135.743428 | 411.670 | 411.670065 |
| 1.2 | Average Power Generation | 458.638 | 458.6384 | 377.065 | 377.0650666666666667 | 381.176 | 381.1759844444444444 |
| 1.3 | Total Export (GT) | 10.429 | 10.429091 | 127.578 | 127.516365 | 386.713 | 386.650908 |
| 1.4 | Total Import (GT) | 0.000 | 0.000000 | 0.062 | 0.061818 | 0.062 | 0.061818 |
| 1.5 | Net Export (GT Export − GT Import) | 10.429 | 10.429 | 127.516 | 127.454 | 386.651 | 386.589 |
| 1.6 | Auxiliary Power Consumption (APC incl Import) | 0.578 | 0.578231 | 8.227 | 8.165245 | 25.019 | 24.957333 |
| 1.7 | APC % | - | 5.250 | - | 6.015 | - | 6.063 |
| 1.8 | Hours on Grid | 1.000 | 1D 0:00 | 14 Day(s), 19 Hrs, 55 Mins | - | 44 Day(s), 19 Hrs, 55 Mins | - |
| 1.9 | Grid Frequency | Min - 49.86 Hz / Max - 50.17 Hz / Avg - 49.98 Hz | Min - 49.860 Hz / Max - 50.170 Hz / Avg - 49.980 Hz | - | - | - | - |

## 2️⃣ PERFORMANCE

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2.1 | Plant Load Factor | 0.874 | 87.360 | 0.718 | 71.821 | 0.726 | 72.604 |
| 2.2 | Partial Loading | 0.126 | 12.640 | 0.282 | 28.179 | 0.274 | 27.396 |
| 2.3 | Plant Availability Factor (SEPC) | 1.000 | - | 0.989 | 0.000 | 0.965 | 0.000 |
| 2.4 | Plant Availability Factor (TNPDCL) | 1.000 | - | 0.990 | 0.000 | 0.965 | 0.000 |
| 2.5 | Plant Outage – Forced | - | 0.000 | - | 0 | - | 0 |
| 2.6 | Plant Outage – Planned | - | 0.000 | - | 0 | - | 0 |
| 2.7 | Plant Outage – RSD | - | 0.000 | - | 0 | - | 0 |
| 2.8 | Specific Oil Consumption | 0.000 | 0.0000 | 0.169 | 0.24639333333333333333 | 0.056 | 0.08213111111111111111 |
| 2.9 | Specific Coal Consumption | 0.000 | 0.0000 | 0.000 | 0.00000000000000000000 | 0.000 | 0.00000000000000000000 |
| 2.10 | GHR (As Fired) | 0 / 420.85 MW | 0.00 | 0.000 | - | 0.000 | - |
| 2.11 | GHR Remarks | - | - | - | - | - | - |
| 2.12 | GCV (As Fired) | 4912.000 | 4891.000 |  | 4962.0000000000000000 |  | 4848.0444444444444444 |

## 3️⃣ CONSUMPTION & STOCK

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3.1 | LDO Consumption | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 3.2 | HFO Consumption | 0.000 | 0.000 | 22.927 | 22.927 | 22.927 | 22.927 |
| 3.3 | Coal Consumption | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 3.4 | LDO Receipt | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 3.5 | HFO Receipt | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 3.6 | Coal Receipt | 0.000 | 0.000 | 90832.300 | 90832.300 | 217587.540 | 217587.540 |
| 3.7 | LDO Total / Usable Stock | 156.5 / 101.5 | 156.500 | - | - | - | - |
| 3.8 | HFO Total / Usable Stock | 707.394 / 197.394 | 707.394 | - | - | - | - |
| 3.9 | Coal Stock | -2146826265.000 | 0.000 | - | - | - | - |
| 3.10 | DM Water Consumption (Cycle Makeup) | 312.570 | 312.570 | 5350.576 | 5350.574 | 14847.478 | 14847.475 |
| 3.11 | Total DM Water Consumption (Plant) | 312.570 | 312.570 | 6308.490 | 6308.490 | 17780.620 | 17780.620 |
| 3.12 | Service Water Consumption | 782.780 | 782.780 | 11171.920 | 11171.920 | 28041.160 | 28041.160 |
| 3.13 | Potable Water Consumption | 41.000 | 41.000 | 613.000 | 613.000 | 1872.000 | 1872.000 |
| 3.14 | Sea Water Consumption | 14500.863 | 14500.863 | 309347.000 | 309347.002 | 952063.432 | 952063.434 |
| 3.15 | H₂ Consumption | - | 84.000 | - | 427 | - | 1218 |
| 3.16 | CO₂ Consumption | - | 0.000 | - | 0 | - | 0 |
| 3.17 | N₂ Consumption | - | 0.000 | - | 0 | - | 0 |
| 3.18 | H₂ Stock | - | 0.000 | - | - | - | - |
| 3.19 | CO₂ Stock | - | 0.000 | - | - | - | - |
| 3.20 | N₂ Stock | - | 0.000 | - | - | - | - |

## 4️⃣ POWER SCHEDULE

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4.1 | Declared Capacity (SEPC) | 11.813 | 11.812560 | 175.327 | 175.327450 | 513.084 | 513.084300 |
| 4.2 | Declared Capacity (TNPDCL) | 11.813 | 11.812560 | 175.327 | 175.327450 | 513.084 | 513.084300 |
| 4.3 | Schedule Generation (SG – PPA) | 10.435 | 10.434650 | 128.743 | 128.742730 | 389.613 | 389.613190 |
| 4.4 | Schedule Generation (SG – DAM) | 0.000 | 0.000000 | 0.000 | 0.000000 | 0.000 | 0.000000 |
| 4.5 | Schedule Generation (SG – RTM) | 0.000 | 0.000000 | 0.000 | 0.000000 | 0.000 | 0.000000 |
| 4.6 | Total Schedule Generation | 10.435 | 10.4346500.0000000.000000 | 128.743 | 128.7427300.0000000.000000 | 389.613 | 389.6131900.0000000.000000 |
| 4.7 | Asking Rate to Achieve 80% DC | MTD | 7.35 | 7.35 MU/day or 306.31 MW or 62.2 % of Full DC | - | - | - |
| 4.8 | Deemed Generation – DG (TB + RSD) | 1.378 | 1.377910 | 46.585 | 46.584720 | 123.471 | 123.471110 |
| 4.9 | DC Loss (Capacity − DC SEPC) | 0.000 | 0.00 | 0.011 | - | 0.035 | - |
| 4.10 | DC Loss Reason – Daily | - |  | - | - | - | - |

## 5️⃣ ASH

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 5.1 | Fly Ash to User | 1107.740 | 1107.740 | 14995.680 | 14995.680 | 40350.540 | 40350.540 |
| 5.2 | Fly Ash to Dyke / Internal | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 5.3 | Bottom Ash to User | 168.040 | 168.040 | 2195.120 | 2195.120 | 5911.740 | 5911.740 |
| 5.4 | Bottom Ash to Dyke / Internal | 0.000 | 0.000 | 0.000 | 0.000 | 90.000 | 90.000 |
| 5.5 | Fly Ash Generated | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 5.6 | Bottom & Eco Ash Generated | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 5.7 | Fly Ash in Silo | 497.630 | 0.000 | - | - | - | - |
| 5.8 | Bottom Ash in Silo | 9.670 | 0.000 | - | - | - | - |

## 6️⃣ WATER

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6.1 | IDCT Make Up (Sea Water) | 65093.801 | 65093.801 | 1526724.072 | 1526724.072 | 4596454.005 | 4596454.004 |
| 6.2 | SWI Flow | 71064.801 | 71064.801 | 1606778.072 | 1606778.072 | 4801659.005 | 4801659.004 |
| 6.3 | Outfall (CT Blowdown & WTP Reject) | 56563.937 | 56563.937 | 1297431.072 | 1297431.072 | 3849595.573 | 3849595.575 |
| 6.4 | Specific Water Consumption | 1.317 | NaN | 2.279 | - | 2.313 | - |
| 6.5 | DM Water Generation | 537.000 | 537.000 | 6399.000 | 6399.000 | 17761.800 | 17761.800 |
| 6.6 | Filtered / Service Water Generation | 852.080 | 852.080 | 11181.820 | 11181.820 | 27575.860 | 27575.860 |
| 6.7 | DM Water Total / Usable Stock | 2311 / 1761 | 2311.120 | - | - | - | - |
| 6.8 | Service Water Total / Usable Stock | 8494 / 6494 | - | - | - | - | - |

## 7️⃣ DSM (Till Date)

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7.1 | DSM Net Profit | 1.379 | 137936.611 | 19.765 | 1297240.457 | 99.236 | 9986109.754 |
| 7.2 | DSM Payable by SEPC | 0.000 | 0.000 | -47.145 | 4953826.500 | -64.877 | 7109371.488 |
| 7.3 | DSM Receivable by SEPC | 0.000 | 15607.670 | 0.000 | 136018.850 | 6.533 | 1147769.885 |
| 7.4 | DSM Coal Saving / (+Loss) by SEPC | - | 122328.941 | - | 6115048.107 | - | 15947711.357 |

## 8️⃣ URS PROFIT / LOSS

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 8.1 | URS Net Profit | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |

## 9️⃣ DC LOSS B/U (Capacity – DC TNPDCL)

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 9.1 | Coal Shortage | 0 / 0 | - | 0 / 0 | 0 / 0.00000000000000000000% | 16.62 / 3.13 | 16.6200 / 7.7340000000000000% |
| 9.2 | CRE to SMPS Failure Trip | - | - | - | 1.8609 / 1.86000000000000000000% | - | 1.8609 / 0.37200000000000000000% |
| 9.3 | Bunker Choke | 0 / 0 | - | 0 / 0 | 0 / 0.00000000000000000000% | 0 / 0 | 0 / 0.00000000000000000000% |
| 9.4 | AOH | - | - | - | 0 / 0.00000000000000000000% | - | 0 / 0.00000000000000000000% |
| 9.5 | Low Vacuum Trip | - | - | - | 0 / 0.00000000000000000000% | - | 0 / 0.00000000000000000000% |

## 🔟 ACTIVITIES / REMARKS

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 10.1 | Major Activities | - | Boiler 1. ID Fan- A&B Lop Schedule Change over Done from B to A. 2. DC scanner air fan trial taken found ok. 3. FDF A&B, PAF A&B standby LOP trial taken found normal. Turbine 1. AWU-3 pump-1 PM work completed. 2. CWPH external oil purifier PM work completed. AHP 1. Ash conditioner water pump #1 surrendered . DOR checking done. Found ok. Running Equipments: BOILER: Mill B,C,D,E,F BCP A & C, IDF A&B, FDF A&B, PAF A&B, SAF A, APH A2, B2 TURBINE : TDBFP A,B CEP B,C SGDMCW B, TGDMCW A & C, CWP A,C ACSOP-1, HPCF B, PW Pump-B BOP: SWIP -B , HVAC Chiller 2, SAC-A, FF Jockey 1, SCC-2 External Filtration Units Running: 1. HPCF external Klarol stop condition. 2. MOT Klarol filter running condition. 3. TDBFP - B klarol filter running condition 4. MDBFP - Portable centrifuge running condition. 5. ID Fan B External filter unit running condition. 6. MOT Centrifuge running condition. 7. TDBFP-A Centrifuge running condition. 8. TDBFP-B Centrifuge running condition. 9. Mill -F External filter unit running condition. 10. CWP-C External filter running 1. IP Turbine inner casing metal temperature showing bad value in DCS. 2. ID FAN A inlet gate 2 / 10-10-2022 / gear box tooth damaged . Awaiting for new gear box. 3. Furnace camera LHS & RHS / 01-12-2022 / Sent for repair / received LHS camera and fixed, working normal 4. MSSV - 2 RHS MOV body crack observed and M seal applied. 5. TDBFP - A booster pump thrust bearing metal temperature 1 to 4 not working. 6. TDBFP - B turbine thrust bearing metal temperature 2 nos not working. 7. Air Washer Unit-1 Blower-1 impeller found damage / 21.06.2024. 8. TDBFP-A exhaust steam pressure transmitter (3 Nos) Showing different values/23.09.2024 9. Fire Tender-01 / 03-02-2025 / left to ABT service center, for tinkering work purpose. 10. GT Yard Oil/water transfer Water Pump-2 jammed condition/08.04.20 11. APH-A Outlet Flue Gas temperature transmitter (1HNA30CT002_XQ02) Showing wrong value/04.05.2025 12. ESP Package AC-4 Compressor-2 HP Fault alarm/10.05.2025/ gas filled and taken in service running normal. | - | - | - | - |
| 10.2 | Remarks | - |  | - | - | - | - |
| 10.3 | Observations | - |  | - | - | - | - |

# VALIDATION DATE: 2025-06-12

## 1️⃣ POWER

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1.1 | Power Generation | 0.000 | 0.000000 | 97.973 | 97.972636 | 528.980 | 528.979692 |
| 1.2 | Average Power Generation | 0.000 | 0.0000 | 340.183 | 340.1827583333333333 | 301.929 | 301.9290465753424658 |
| 1.3 | Total Export (GT) | 0.000 | 0.000000 | 92.349 | 92.174546 | 497.142 | 496.800000 |
| 1.4 | Total Import (GT) | 0.215 | 0.214545 | 0.389 | 0.389091 | 1.749 | 1.749093 |
| 1.5 | Net Export (GT Export − GT Import) | -0.215 | -0.214 | 91.960 | 91.785 | 495.393 | 495.051 |
| 1.6 | Auxiliary Power Consumption (APC incl Import) | 0.215 | 0.000000 | 6.013 | 5.623547 | 33.587 | 31.837871 |
| 1.7 | APC % | - | 0.000 | - | 5.740 | - | 6.019 |
| 1.8 | Hours on Grid | 0.000 | 1D 0:00 | 10 Day(s), 1 Hrs, 40 Mins | - | 57 Day(s), 7 Hrs, 56 Mins | - |
| 1.9 | Grid Frequency | Min - 0 Hz / Max - 0 Hz / Avg - 0 Hz | Min - 0.000 Hz / Max - 0.000 Hz / Avg - 0.000 Hz | - | - | - | - |

## 2️⃣ PERFORMANCE

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2.1 | Plant Load Factor | 0.000 | 0.000 | 0.648 | 64.797 | 0.575 | 57.510 |
| 2.2 | Partial Loading | 1.000 | - | 0.352 | 35.203 | 0.425 | 42.490 |
| 2.3 | Plant Availability Factor (SEPC) | 0.000 | - | 0.910 | 0.000 | 0.964 | 0.000 |
| 2.4 | Plant Availability Factor (TNPDCL) | 0.000 | - | 0.910 | 0.000 | 0.964 | 0.000 |
| 2.5 | Plant Outage – Forced | - | 0.000 | - | 0 | - | 0 |
| 2.6 | Plant Outage – Planned | - | 0.000 | - | 0 | - | 0 |
| 2.7 | Plant Outage – RSD | - | 0.000 | - | 0 | - | 0 |
| 2.8 | Specific Oil Consumption | 0.000 | - | 1.738 | 29.7120818181818182 | 0.365 | 5.6021830508474576 |
| 2.9 | Specific Coal Consumption | 0.000 | - | 0.000 | 0.00000000000000000000 | 0.000 | 0.00000000000000000000 |
| 2.10 | GHR (As Fired) | 0 / 311.82 MW | - | 0.000 | - | 0.000 | - |
| 2.11 | GHR Remarks | - | - | - | - | - | - |
| 2.12 | GCV (As Fired) | 4716.000 | 0.000 |  | 4393.0833333333333333 |  | 3912.4246575342465753 |

## 3️⃣ CONSUMPTION & STOCK

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3.1 | LDO Consumption | 0.000 | 0.000 | 41.688 | 41.688 | 41.688 | 41.688 |
| 3.2 | HFO Consumption | 0.000 | 0.000 | 128.566 | 128.566 | 151.493 | 151.493 |
| 3.3 | Coal Consumption | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 3.4 | LDO Receipt | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 3.5 | HFO Receipt | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 3.6 | Coal Receipt | 7435.080 | 7435.080 | 69293.080 | 69293.080 | 286880.620 | 286880.620 |
| 3.7 | LDO Total / Usable Stock | 114.812 / 59.812 | 114.812 | - | - | - | - |
| 3.8 | HFO Total / Usable Stock | 578.828 / 68.828 | 578.828 | - | - | - | - |
| 3.9 | Coal Stock | -2146826265.000 | 0.000 | - | - | - | - |
| 3.10 | DM Water Consumption (Cycle Makeup) | 63.261 | 63.261 | 3886.237 | 3886.237 | 19878.067 | 19878.065 |
| 3.11 | Total DM Water Consumption (Plant) | 428.260 | 428.260 | 5089.320 | 5089.320 | 24515.000 | 24515.000 |
| 3.12 | Service Water Consumption | 1628.135 | 1628.135 | 9165.370 | 9165.370 | 50234.520 | 50234.520 |
| 3.13 | Potable Water Consumption | 60.000 | 60.000 | 496.000 | 496.000 | 2958.000 | 2958.000 |
| 3.14 | Sea Water Consumption | 2208.230 | 2208.230 | 241816.452 | 241816.451 | 1265454.984 | 1265454.985 |
| 3.15 | H₂ Consumption | - | 0.000 | - | 175 | - | 1582 |
| 3.16 | CO₂ Consumption | - | 0.000 | - | 0 | - | 0 |
| 3.17 | N₂ Consumption | - | 0.000 | - | 0 | - | 0 |
| 3.18 | H₂ Stock | - | 0.000 | - | - | - | - |
| 3.19 | CO₂ Stock | - | 0.000 | - | - | - | - |
| 3.20 | N₂ Stock | - | 0.000 | - | - | - | - |

## 4️⃣ POWER SCHEDULE

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4.1 | Declared Capacity (SEPC) | 0.000 | 0.000000 | 129.052 | 129.051750 | 831.137 | 831.137010 |
| 4.2 | Declared Capacity (TNPDCL) | 0.000 | 0.000000 | 129.052 | 129.051750 | 831.137 | 831.137010 |
| 4.3 | Schedule Generation (SG – PPA) | 0.000 | 0.000000 | 92.462 | 92.461800 | 500.174 | 500.173690 |
| 4.4 | Schedule Generation (SG – DAM) | 0.000 | 0.000000 | 0.000 | 0.000000 | 0.000 | 0.000000 |
| 4.5 | Schedule Generation (SG – RTM) | 0.000 | 0.000000 | 0.000 | 0.000000 | 0.000 | 0.000000 |
| 4.6 | Total Schedule Generation | 0.000 | 0.0000000.0000000.000000 | 92.462 | 92.4618000.0000000.000000 | 500.174 | 500.1736900.0000000.000000 |
| 4.7 | Asking Rate to Achieve 80% DC | MTD | 8.58 | 8.58 MU/day or 357.52 MW or 72.6 % of Full DC | - | - | - |
| 4.8 | Deemed Generation – DG (TB + RSD) | 0.000 | 0.000000 | 36.590 | 36.589950 | 330.963 | 330.963320 |
| 4.9 | DC Loss (Capacity − DC SEPC) | 1.000 | 0.000 | 0.090 | - | 0.036 | - |
| 4.10 | DC Loss Reason – Daily | - |  | - | - | - | - |

## 5️⃣ ASH

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 5.1 | Fly Ash to User | 485.200 | 485.200 | 10743.380 | 10743.380 | 53541.320 | 53541.320 |
| 5.2 | Fly Ash to Dyke / Internal | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 5.3 | Bottom Ash to User | 51.060 | 51.060 | 2102.140 | 2102.140 | 8658.480 | 8658.480 |
| 5.4 | Bottom Ash to Dyke / Internal | 0.000 | 0.000 | 60.000 | 60.000 | 150.000 | 150.000 |
| 5.5 | Fly Ash Generated | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 5.6 | Bottom & Eco Ash Generated | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 5.7 | Fly Ash in Silo | 331.750 | 0.000 | - | - | - | - |
| 5.8 | Bottom Ash in Silo | 0.000 | 0.000 | - | - | - | - |

## 6️⃣ WATER

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6.1 | IDCT Make Up (Sea Water) | 0.000 | 0.000 | 1177037.024 | 1177037.025 | 6074674.906 | 6074674.906 |
| 6.2 | SWI Flow | 7817.000 | 7817.000 | 1240899.024 | 1240899.025 | 6411486.906 | 6411486.906 |
| 6.3 | Outfall (CT Blowdown & WTP Reject) | 5608.770 | 5608.770 | 999082.572 | 999082.574 | 5146031.923 | 5146031.926 |
| 6.4 | Specific Water Consumption | 0.000 | - | 2.468 | - | 2.392 | - |
| 6.5 | DM Water Generation | 480.000 | 480.000 | 5076.600 | 5076.600 | 24562.760 | 24562.760 |
| 6.6 | Filtered / Service Water Generation | 1668.230 | 1668.230 | 10236.550 | 10236.550 | 50315.700 | 50315.700 |
| 6.7 | DM Water Total / Usable Stock | 2378 / 1828 | 2377.700 | - | - | - | - |
| 6.8 | Service Water Total / Usable Stock | 9041 / 7041 | - | - | - | - | - |

## 7️⃣ DSM (Till Date)

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7.1 | DSM Net Profit | 0.000 | - | 8.387 | 1182401.845 | 114.786 | 11594114.204 |
| 7.2 | DSM Payable by SEPC | 0.000 | - | 0.000 | 479098.603 | -64.877 | 7629072.661 |
| 7.3 | DSM Receivable by SEPC | 0.000 | - | 4.813 | 581896.792 | 12.266 | 2084491.797 |
| 7.4 | DSM Coal Saving / (+Loss) by SEPC | - | - | - | 1079603.656 | - | 17138695.068 |

## 8️⃣ URS PROFIT / LOSS

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 8.1 | URS Net Profit | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |

## 9️⃣ DC LOSS B/U (Capacity – DC TNPDCL)

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 9.1 | Coal Shortage | 0 / 0 | - | 0 / 0 | 0 / 0.00000000000000000000% | 16.62 / 1.93 | 16.6200 / 4.8337500000000000% |
| 9.2 | CRE to SMPS Failure Trip | - | - | - | 0 / 0.00000000000000000000% | - | 1.8609 / 0.23250000000000000000% |
| 9.3 | Bunker Choke | 0 / 0 | - | 0.48 / 0.34 | 0.4842 / 0.48000000000000000000% | 0.48 / 0.06 | 0.4842 / 0.18000000000000000000% |
| 9.4 | AOH | - | 11.8126 / 12.21% | - | 12.2148 / 4.2033333333333333% | - | 12.2148 / 1.5762500000000000% |
| 9.5 | Low Vacuum Trip | - | - | - | 0 / 0.00000000000000000000% | - | 0 / 0.00000000000000000000% |

## 🔟 ACTIVITIES / REMARKS

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 10.1 | Major Activities | - | Boiler 1. APH A&B Water Washing completed 08:50 hrs 2. ID FAN-B Started @09:15 hrs, FD FAN-A Started @10:56 hrs for force cooling. Turbine 1. Generator H2 was purging CO2, and CO2 was purged using instrument air. Now air pressure kept as 3.45 ksc. A total of 27 CO2 cylinders was consumed, and one CO2 cylinder observed gas leak in the valve gland area (number 84287). 2. CO2 empty cylinders 27 and one Co2 Defective cylinder total 28 cylinders and H2 empty cylinder 27 (FS 20/YARD 07)sent to store for filling purpose 3. Central oil purifier separator motor NO-load trial taken in front of MTP & TMD, vibration readings taken by MTP, BOP 1. APH Water wash transfer pump-2 Coupling completed. PTW Surrendered for Trial Running Equipments: BOILER: Mill B,C,D,E BCP A & C, IDF A&B, FDF A&B, PAF A&B, SAF B, APH A2, B1 TURBINE : TDBFP A,B CEP A,C SGDMCW A, TGDMCW A & B, CWP A,B, ACSOP-2, HPCF A, PW Pump-B BOP: SWIP -A , HVAC Chiller 2, SAC-A, FF Jockey 1, SCC-1 External Filtration Units Running: 1. HPCF external Klarol running condition. 2. MOT Klarol filter running condition. 3. TDBFP - B klarol filter running condition 4. MDBFP - Portable centrifuge running condition. 5. ID Fan B External filter unit running condition. 6. MOT Centrifuge running condition. 7. TDBFP-A Centrifuge stop condition. 8. TDBFP-B Centrifuge running condition. 9. Mill -F External filter unit running condition. 10. CWP-C External filter running 1. IP Turbine inner casing metal temperature showing bad value in DCS. 2. ID FAN A inlet gate 2 / 10-10-2022 / gear box new one replaced, Limit setting completed. 3. Furnace camera LHS & RHS / 01-12-2022 / Sent for repair / received LHS camera and fixed, working normal 4. MSSV - 2 RHS MOV body crack observed and M seal applied. 5. TDBFP - A booster pump thrust bearing metal temperature 1 to 4 not working. 6. TDBFP - B turbine thrust bearing metal temperature 2 nos not working. 7. Air Washer Unit-1 Blower-1 impeller found damage / 21.06.2024. 8. TDBFP-A exhaust steam pressure transmitter (3 Nos) Showing different values/23.09.2024 9. GT Yard Oil/water transfer Water Pump-2 jammed condition/08.04.20 10. APH-A Outlet Flue Gas temperature transmitter (1HNA30CT002_XQ02) Showing wrong value/04.05.2025 11. AWU-3 Fan1 impeller damaged/19.05.2025 12. Chimey lift power cable damage/19.05.2025 13. GIS High mast light tripped/ 21.05.2025 | - | - | - | - |
| 10.2 | Remarks | - |  | - | - | - | - |
| 10.3 | Observations | - |  | - | - | - | - |

# VALIDATION DATE: 2025-07-28

## 1️⃣ POWER

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1.1 | Power Generation | 0.000 | 0.000000 | 0.000 | 0.000000 | 528.980 | 528.979692 |
| 1.2 | Average Power Generation | 0.000 | 0.0000 | 0.000 | 0.00000000000000000000 | 185.217 | 185.2169781512605042 |
| 1.3 | Total Export (GT) | 0.000 | 0.000000 | 0.000 | 0.000000 | 497.142 | 496.800000 |
| 1.4 | Total Import (GT) | 0.211 | 0.210909 | 1.498 | 1.498181 | 3.807 | 3.807274 |
| 1.5 | Net Export (GT Export − GT Import) | -0.211 | -0.211 | -1.498 | -1.498 | 493.335 | 492.993 |
| 1.6 | Auxiliary Power Consumption (APC incl Import) | 0.211 | 0.000000 | 1.498 | 0.000000 | 35.645 | 31.837871 |
| 1.7 | APC % | - | 0.000 | - | 0.000 | - | 6.019 |
| 1.8 | Hours on Grid | 0.000 | 1D 0:00 | 0 Day(s), 0 Hrs, 0 Mins | - | 57 Day(s), 7 Hrs, 56 Mins | - |
| 1.9 | Grid Frequency | Min - 0 Hz / Max - 0 Hz / Avg - 0 Hz | Min - 0.000 Hz / Max - 0.000 Hz / Avg - 0.000 Hz | - | - | - | - |

## 2️⃣ PERFORMANCE

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2.1 | Plant Load Factor | 0.000 | 0.000 | 0.000 | 0.000 | 0.353 | 35.279 |
| 2.2 | Partial Loading | 1.000 | - | 1.000 | - | 0.647 | 64.721 |
| 2.3 | Plant Availability Factor (SEPC) | 0.000 | - | 0.000 | 0.000 | 0.591 | 0.000 |
| 2.4 | Plant Availability Factor (TNPDCL) | 0.000 | - | 0.000 | 0.000 | 0.591 | 0.000 |
| 2.5 | Plant Outage – Forced | - | 0.000 | - | 0 | - | 0 |
| 2.6 | Plant Outage – Planned | - | 0.000 | - | 0 | - | 0 |
| 2.7 | Plant Outage – RSD | - | 0.000 | - | 0 | - | 0 |
| 2.8 | Specific Oil Consumption | 0.000 | - | 0.000 | 0.000 | 0.365 | 5.6021830508474576 |
| 2.9 | Specific Coal Consumption | 0.000 | - | 0.000 | 0.000 | 0.000 | 0.00000000000000000000 |
| 2.10 | GHR (As Fired) | 0 / 0 MW | - | 0.000 | - | 0.000 | - |
| 2.11 | GHR Remarks | - | - | - | - | - | - |
| 2.12 | GCV (As Fired) | - | 0.000 |  | 0.00000000000000000000 |  | 2400.0588235294117647 |

## 3️⃣ CONSUMPTION & STOCK

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3.1 | LDO Consumption | 0.000 | 0.000 | 0.000 | 0.000 | 41.688 | 41.688 |
| 3.2 | HFO Consumption | 0.000 | 0.000 | 0.000 | 0.000 | 151.493 | 151.493 |
| 3.3 | Coal Consumption | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 3.4 | LDO Receipt | 20.000 | 20.000 | 73.000 | 73.000 | 73.000 | 73.000 |
| 3.5 | HFO Receipt | 183.865 | 176.510 | 227.938 | 218.820 | 227.938 | 218.820 |
| 3.6 | Coal Receipt | 0.000 | 0.000 | 0.000 | 0.000 | 355003.360 | 355003.360 |
| 3.7 | LDO Total / Usable Stock | 187.812 / 132.812 | 187.812 | - | - | - | - |
| 3.8 | HFO Total / Usable Stock | 806.766 / 296.766 | 806.766 | - | - | - | - |
| 3.9 | Coal Stock | -2146826265.000 | 0.000 | - | - | - | - |
| 3.10 | DM Water Consumption (Cycle Makeup) | 31.840 | 31.840 | 2561.538 | 2561.540 | 23109.121 | 23109.120 |
| 3.11 | Total DM Water Consumption (Plant) | 31.840 | 31.840 | 2632.000 | 2632.000 | 27915.710 | 27915.710 |
| 3.12 | Service Water Consumption | 248.000 | 248.000 | 9572.420 | 9572.420 | 66668.750 | 66668.750 |
| 3.13 | Potable Water Consumption | 46.000 | 46.000 | 1231.000 | 1231.000 | 4914.000 | 4914.000 |
| 3.14 | Sea Water Consumption | 0.000 | 0.000 | 0.000 | 0.000 | 1265825.124 | 1265825.125 |
| 3.15 | H₂ Consumption | - | 0.000 | - | 0 | - | 1582 |
| 3.16 | CO₂ Consumption | - | 0.000 | - | 0 | - | 0 |
| 3.17 | N₂ Consumption | - | 0.000 | - | 0 | - | 0 |
| 3.18 | H₂ Stock | - | 0.000 | - | - | - | - |
| 3.19 | CO₂ Stock | - | 0.000 | - | - | - | - |
| 3.20 | N₂ Stock | - | 0.000 | - | - | - | - |

## 4️⃣ POWER SCHEDULE

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 4.1 | Declared Capacity (SEPC) | 0.000 | 0.000000 | 0.000 | 0.000000 | 831.137 | 831.137010 |
| 4.2 | Declared Capacity (TNPDCL) | 0.000 | 0.000000 | 0.000 | 0.000000 | 831.137 | 831.137010 |
| 4.3 | Schedule Generation (SG – PPA) | 0.000 | 0.000000 | 0.000 | 0.000000 | 500.174 | 500.173690 |
| 4.4 | Schedule Generation (SG – DAM) | 0.000 | 0.000000 | 0.000 | 0.000000 | 0.000 | 0.000000 |
| 4.5 | Schedule Generation (SG – RTM) | 0.000 | 0.000000 | 0.000 | 0.000000 | 0.000 | 0.000000 |
| 4.6 | Total Schedule Generation | 0.000 | 0.0000000.0000000.000000 | 0.000 | 0.0000000.0000000.000000 | 500.174 | 500.1736900.0000000.000000 |
| 4.7 | Asking Rate to Achieve 80% DC | MTD | - | Asking Rate Crossed the Unit Capacity | - | - | - |
| 4.8 | Deemed Generation – DG (TB + RSD) | 0.000 | 0.000000 | 0.000 | 0.000000 | 330.963 | 330.963320 |
| 4.9 | DC Loss (Capacity − DC SEPC) | 1.000 | 0.000 | 1.000 | - | 0.409 | - |
| 4.10 | DC Loss Reason – Daily | - |  | - | - | - | - |

## 5️⃣ ASH

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 5.1 | Fly Ash to User | 0.000 | 0.000 | 0.000 | 0.000 | 53541.320 | 53541.320 |
| 5.2 | Fly Ash to Dyke / Internal | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 | 0.000 |
| 5.3 | Bottom Ash to User | 0.000 | 0.000 | 0.000 | 0.000 | 8658.480 | 8658.480 |
| 5.4 | Bottom Ash to Dyke / Internal | 0.000 | 0.000 | 0.000 | 0.000 | 150.000 | 150.000 |
| 5.5 | Fly Ash Generated | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 5.6 | Bottom & Eco Ash Generated | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |
| 5.7 | Fly Ash in Silo | 331.750 | 0.000 | - | - | - | - |
| 5.8 | Bottom Ash in Silo | 0.000 | 0.000 | - | - | - | - |

## 6️⃣ WATER

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 6.1 | IDCT Make Up (Sea Water) | 0.000 | 0.000 | 0.000 | 0.000 | 6074674.906 | 6074674.906 |
| 6.2 | SWI Flow | 0.000 | 0.000 | 0.000 | 0.000 | 6413527.906 | 6413527.906 |
| 6.3 | Outfall (CT Blowdown & WTP Reject) | 0.000 | 0.000 | 0.000 | 0.000 | 5147702.783 | 5147702.786 |
| 6.4 | Specific Water Consumption | 0.000 | - | 0.000 | - | 2.393 | - |
| 6.5 | DM Water Generation | 0.000 | 0.000 | 2298.570 | 2298.570 | 27307.250 | 27307.250 |
| 6.6 | Filtered / Service Water Generation | 485.600 | 485.600 | 7068.710 | 7068.710 | 62857.250 | 62857.250 |
| 6.7 | DM Water Total / Usable Stock | 1761 / 1211 | 1761.150 | - | - | - | - |
| 6.8 | Service Water Total / Usable Stock | 5148 / 3148 | - | - | - | - | - |

## 7️⃣ DSM (Till Date)

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 7.1 | DSM Net Profit | 0.000 | - | 0.000 | 0.000 | 118.223 | 11594114.204 |
| 7.2 | DSM Payable by SEPC | 0.000 | - | 0.000 | 0.000 | -68.662 | 7629072.661 |
| 7.3 | DSM Receivable by SEPC | 0.000 | - | 0.000 | 0.000 | 12.266 | 2084491.797 |
| 7.4 | DSM Coal Saving / (+Loss) by SEPC | - | - | - | 0.000 | - | 17138695.068 |

## 8️⃣ URS PROFIT / LOSS

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 8.1 | URS Net Profit | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 | -2146826265.000 | 0.000 |

## 9️⃣ DC LOSS B/U (Capacity – DC TNPDCL)

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 9.1 | Coal Shortage | 0 / 0 | - | 0 / 0 | 0 / 0.00000000000000000000% | 16.62 / 1.18 | 16.6200 / 0.71611111111111111111% |
| 9.2 | CRE to SMPS Failure Trip | - | - | - | 0 / 0.00000000000000000000% | - | 1.8609 / 0.03444444444444444444% |
| 9.3 | Bunker Choke | 0 / 0 | - | 0 / 0 | 0 / 0.00000000000000000000% | 0.48 / 0.03 | 0.4842 / 0.18666666666666666667% |
| 9.4 | AOH | - | 11.8126 / 330.75% | - | 330.7528 / 171.2825000000000000% | - | 555.5944 / 130.5248148148148148% |
| 9.5 | Low Vacuum Trip | - | - | - | 0 / 0.00000000000000000000% | - | 0 / 0.00000000000000000000% |

## 🔟 ACTIVITIES / REMARKS

| S.N | Particulars | Excel Daily | App Daily | Excel MTD | App MTD | Excel YTD | App YTD |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 10.1 | Major Activities | - | Boiler: 1. IDF A Load Trial taken. Found normal. 2. PA Fan-B trial taken, found normal. 3. Mill-B load trial taken, scrapper inside abnormal noise observed. So stopped. Turbine: 1. CEP-B trial taken. 2. TDBFP-A LOP & JOP started and barring gear taken in service. BOP: 1. SWIP-A load trial taken and found. Running Equipments: PWP B, AC SOP 1, SGDMCW-B, TDBFP-B, MOT Centrifuge running condition. 1. IP Turbine inner casing metal temperature showing bad value in DCS. 2. ID FAN A inlet gate 2 / 10-10-2022 / gear box new one replaced, Limit setting completed. 3. Furnace camera LHS & RHS / 01-12-2022 / Sent for repair / received LHS camera and fixed, working normal 4. MSSV - 2 RHS MOV body crack observed and M seal applied. 5. TDBFP - A booster pump thrust bearing metal temperature 1 to 4 not working. 6. TDBFP - B turbine thrust bearing metal temperature 2 nos not working. 7. Air Washer Unit-1 Blower-1 impeller found damage / 21.06.2024. 8. TDBFP-A exhaust steam pressure transmitter (3 Nos) Showing different values/23.09.2024 9. GT Yard Oil/water transfer Water Pump-2 jammed condition/08.04.20 10. APH-A Outlet Flue Gas temperature transmitter (1HNA30CT002_XQ02) Showing wrong value/04.05.2025 11. AWU-3 Fan1 impeller damaged/19.05.2025 12. Chimey lift power cable damage/19.05.2025 13. GIS High mast light tripped/ 21.05.2025 | - | - | - | - |
| 10.2 | Remarks | - |  | - | - | - | - |
| 10.3 | Observations | - |  | - | - | - | - |